Solaronics, Inc., Gas Fired Infrared Radiant Heaters Customizable Master Word Specifications. These specifications are provided to assist in specifying Solaronics, Inc. products.  A qualified design professional should review and edit the specifications to satisfy project requirements. For more information, contact: Solaronics, Inc., 3720 Lapeer Road, Auburn Hills, Michigan MI 48326; phone: 248-651-5333, fax: 248-651-0357, website: www.solaronicsusa.com, email: sales@solaronicsusa.com.

SECTION 23 55 23 - GAS-FIRED RADIANT HEATERS (FORMERLY SECTION 15542)

PART 1 - GENERAL

1.1	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions, and Division 01 Specification Sections apply to this Section.

1.2	SUMMARY

A.	Section includes:

1.	[Gas-Fired Infrared Radiant Tube Heaters.]

B.	Related Sections:

1.	Division 23, Section 23 10 00 "Facility Fuel Systems".

2.	Division 23, Section 23 51 00 "Breechings, Chimneys, and Stacks".

3.	Division 26, Section 26 05 00 "Common Work Results for Electrical".

1.3	REFERENCES

A.	Applicable Standards:

1.	American National Standards Institute (ANSI):

a.	Z83.19 - Gas-Fired High-Intensity Infrared Heaters.

b.	Z83.20 - Gas-Fired Low-Intensity Infrared Heaters.

2.	National Fire Protection Association (NFPA):

a.	54 - National Fuel Gas Code.

b.	70 - National Electric Code.

3.	Underwriters Laboratories Inc. (UL):

a.	486A - Wire Connectors and Soldering Lugs for Use with Copper Conductors.

b.	486B - Wire Connectors for Use with Aluminum Conductors.

1.4	SUBMITTALS

A.	Product Data: Include rated capacities, operating characteristics, physical dimensions, weights, furnished specialties, and accessories.

B.	Shop Drawings: Include field wiring diagrams of power, signal, and control wiring.

C.	Coordination Drawings: Include anchorages and attachments to structure and to supported equipment based on input from equipment installers.

D.	Field Quality-Control Test Reports: From Contractor.

E.	Operation and Maintenance Data: For gas-fired radiant heaters include installation, operation and maintenance manuals.

F.	Warranties: Special warranties specified in this Section.

1.5	QUALITY ASSURANCE

A.	Building Codes and Standards.

1.	[Gas-Fired Low-Intensity Infrared Radiant Tube Heaters shall be Design Certified by CSA to ANSI Z83.20. The supplier shall provide the CSA Certification Number and the heaters shall bear the CSA Seal of Certification.]

2.	Heaters shall comply with current Occupational Safety and Health (OSHA) Requirements.

3.	Heaters shall be furnished and installed in accordance with NFPA 54, local codes, building drawings and manufacturer's recommendations.

4.	Natural or mechanical means shall be provided to supply and exhaust at least 4 CFM per 1000 Btu/hour input of installed heaters.

5.	In locations used for the storage of combustible materials, signs shall be posted to specify the maximum permissible stacking height to maintain required clearances from the heater to the combustibles.

B.	Source Limitations: Obtain gas-fired radiant heaters through one source from a single manufacturer.

C.	Product Options: Drawings indicate size, profiles, and dimensional requirements of gas-fired radiant heaters and are based on the specific system indicated. Refer to Division 1, Section "Product Requirements."

D.	Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.6	WARRANTY

A.	Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of gas-fired radiant heater that fails in materials or workmanship within specified warranty period.

B.	Warranty Period:

1.	Gas-Fired Infrared Radiant Tube Heaters:

a.	[MT and ST models: Ten (10) years on the heater's burner core, heat exchanger, and combustion chamber tubes; and two (2) years on all the heater control assembly components.]

b.	[SMT and SST models: Ten (10) years on the heater's burner core, five (5) years on the heat exchanger, and combustion chamber tubes; and one (1) year on all the heater control assembly components.]

c.	[MTSA/MTUA and GQ models: Ten (10) years on the heater's burner core, five (5) years on the heat exchanger, and combustion chamber tubes; and two (2) years on all the heater control assembly components.]

PART 2 - PRODUCTS

2.1	MANUFACTURERS

A.	In other Part 2 articles where subparagraph titles below introduce lists, the following requirements apply for product selection:

1.	Manufacturers: Subject to compliance with requirements, provide products by the manufacturers specified.

2.2	GAS-FIRED LOW INTENSITY INFRARED RADIANT TUBE HEATERS  (SECTION 235523.13)

A.	Manufacturers:

1.	Solaronics, Inc. - Basis of design specification.

a.	Heaters shall be SOLARONICS:

i.	[TRUE DUAL MT-SERIES (2-stage)],

ii.	[SUNTUBE IV VERSAMOUNT ST-SERIES (single-stage)],

iii.	[STAINLESS-STEEL TRUE DUAL SMT-SERIES (2-stage)],

- [STAINLESS-STEEL SUNTUBE IV SST-SERIES (single-stage)],

- [ALUMINIZED TRUE DUAL MTUA/MTSA-SERIES (2-stage)], or

vi.	[SUNTUBE IV GLOBAL QUALITY GQ-SERIES (single-stage)]

b.	Gas-Fired Infrared Radiant Tube Heaters of: series model numbers, inputs in MBTUH, lengths and configurations;

c.	Manufactured by Solaronics, Inc., Rochester, Michigan 48307; or comparable product by the following:

2.	Or equal.

B.	Description: Heater factory assembled, piped, wired, fully tested and ready to install and complying with ANSI Z83.20.

1.	[2-Stage Control: Heaters shall provide 2-stage control of Both Gas and Air for the most efficient and complete combustion at both high and low-fire rates.]

a.	[Performance: Highest possible emitter/heat exchanger temperature at both high-fire and low-fire rates for higher radiant efficiency and lower fuel usage.]

b.	[Benefits: Stop energy overshoot, improve comfort, cut energy consumption, and provide more heat quickly when temperature falls sharply.]

- CSA Approval: Heater Design Certified by and bearing the label of CSA (formerly AGA, the American Gas Association).

- For commercial / industrial use.

- For either indoor or outdoor installation.

- For vented or unvented use.

3.	Type of Gas: Heater designed and built to burn fuel gas with characteristics same as those of gas available at project site.

a.	[Natural Gas: Heaters designed to operate without adjustments when burning natural gas having a heat value of 1000 BTU per cubic foot with a specific gravity of .65.]

b.	[Propane Gas: Heaters designed to operate without adjustments when burning propane gas having a heat value of 2500 BTU per cubic foot with a specific gravity of 1.53.]

4.	Supply Inlet Gas Pressure:

a.	[Natural Gas: Heaters designed to satisfactorily operate on natural gas at a minimum supply inlet gas pressure of 7 inches water column (W.C.) and at a maximum supply inlet gas pressure of 14 inches W.C.]

b.	[Propane Gas: Heaters designed to satisfactorily operate on propane gas at a minimum supply inlet gas pressure of 11 inches water column (W.C.) and at a maximum supply inlet gas pressure of 14 inches W.C.]

C.	Burner Safety Controls:

1.	Gas Control Valve:

a.	[2-stage, regulated redundant-solenoid 24-VAC electric gas valve containing pressure regulator and manual shutoff in one body, and no pilot.]

b.	[Single-stage, regulated redundant-solenoid 115-VAC electric gas valve containing pressure regulator, and no pilot.]

2.	Blocked Vent Safety: Differential pressure switch in burner safety circuit to stop burner operation with high discharge pressure or insufficient combustion air.

3.	Indicator Lights: Burner-on indicator light.

- Safety Shutoff: Automatic shut-off of gas flow to burner when gas supply or power supply interrupted.

D.	Burner Type: Non-condensing, gravity-vented or sidewall-vented, power gas burner, with the following features:

1.	Burner CSA certified for use in unvented mode or vented modes with vertical or horizontal vent terminal.

2.	Burner Ignition:

a.	Direct spark ignition with electronic flame safety.

b.	Direct spark ignitor durable to resist breakage.

3.	Burner Core: Assembly of durable materials, for high efficiency complete combustion, maximum heat transfer, extremely quiet operation, and extended life.

4.	Sight glass for burner flame and spark ignitor observation from floor level.

5.	Burner Blower:

a.	Motor: Balanced-rotor, thermally protected, and permanently lubricated.

b.	Blower Impeller: Statically and dynamically balanced.

c.	Capable of drawing in outside combustion air without using additional supply fans.

6.	[MT propane, SMT, MTSA/MTUA propane, ST propane, SST and GQ propane models: Inlet air collar supplied with burner control assembly to accept 4" O.D. supply duct.]

E.	Heater Controls:

1.	[MT, SMT and MTSA/MTUA models: 2-stage operation to include:]

a.	[Operation: 2-stage control Both Gas and Air.]

b.	[Input differential: 30% between low-fire and high-fire rates.]

c.	[Purge Control: 30-second pre-purge and 120-second post-purge to remove products of combustion.]

d.	[Power Thermostat: Provide 24-volt power supply for 2-stage thermostat at heater terminal board.  No additional 24-volt power supply required.]

e.	[Recycle: Automatic recycle after inadvertent shutdown.]

f.	[Self-diagnostics: Ignition module include self-diagnostics and external LED readout.]

2.	[ST, SST and GQ models: Single-stage operation to include:]

a.	[Total heater shutdown upon control lockout, including burner operation and combustion air blower, where power interruption (reset thermostat) restarts firing sequence.]

3.	Direct spark ignition system with three (3) trials-for-ignition and upon loss of flame sensing three (3) re-trials-for-ignition.

4.	Flame Sensing: Independent sensing rod and circuit for reliability.

5.	Controls isolated from combustion air to prevent corrosion from wet/dirty air.

6.	Controls enclosed with a corrosion resistant housing.

7.	Control enclosure permit easy access to controls from three sides by removing cover.

8.	Call for heat signal:

a.	[MT, SMT and MTSA/MTUA models: 24 VAC provided to thermostat by heater itself for both low-heat and high-heat call signals.]

b.	[ST, SST and GQ models: 115 VAC electrical power supply.]

9.	Electrical Power:

a.	Volts: 115 VAC.

b.	Phase: Single.

c.	Hertz: 60 Hz.

d.	Total Maximum Current Draw: 3 Amps.

10.	[MT, MTSA/MTUA, ST and GQ models: Include electrical power cord with 3 copper conductors extending 36 inches from control enclosure with 3-prong plug.]

F.	Combustion Tubing:

1.	[MT, MTSA/MTUA, ST and GQ 65-100 MBTUH models: Combustion chamber tubing of 4-inch diameter, 16 ga. wall thickness, Aluminized 409 Stainless Steel.]

- [Material: Aluminized 409 Stainless Steel tubing coated with corrosion resistant 8% silicon/aluminum alloy, and meet MIL 500 hour salt spray test.]

b.	[Additional coating: tubing finished with a high emissivity rated, corrosion resistant, black coating.]

2.	[MT, MTSA/MTUA, ST and GQ 105-200 MBTUH models: Combustion chamber tubing of 4-inch diameter, 14 ga. wall thickness, Aluminized 409 Stainless Steel.]

- [Material: Aluminized 409 Stainless Steel tubing coated with corrosion resistant 8% silicon/aluminum alloy, and meet MIL 500 hour salt spray test.]

- [Additional coating: tubing finished with a high emissivity rated, corrosion resistant, black coating.]

- [ST and GQ 40-60 MBTUH models: Combustion chamber tubing of 4-inch diameter, 16 ga. wall thickness, Aluminized 409 Stainless Steel.]

a.	[Material: Aluminized 409 Stainless Steel tubing coated with corrosion resistant 8% silicon/aluminum alloy, and meet MIL 500 hour salt spray test.]

b.	[Additional coating: tubing finished with a high emissivity rated, corrosion resistant, black coating.]

4.	[SMT and SST models: Combustion chamber tubing of 4-inch diameter, 16 ga. wall thickness, 304L stainless-steel.]

a.	[Additional coating: tubing finished with a high emissivity rated, corrosion resistant, black coating.]

G.	Emitter/Heat Exchanger Tubing:

1.	Non-Condensing Emitter: No condensation forms from combustion in emitter/heat exchanger tubing while at operating temperatures.

2.	Heaters utilize downstream turbulator, factory installed, in the last 10-foot long emitter/heat exchanger section.

a.	Turbulator wave formed for optimal thermal efficiency.

3.	[MT and ST models Standard: Heat exchanger tubing of 4-inch diameter, 12 ga. (.109") wall thickness, black hot-rolled-steel.]

4.	[MT and ST models Alternate: Heat exchanger tubing of all Aluminized 409 Stainless Steel finished with a high emissivity rated, corrosion resistant, black coating.]

- [Material: Aluminized 409 Stainless Steel tubing coated with corrosion resistant 8% silicon/aluminum alloy, and meet MIL 500 hour salt spray test.]

- [Additional coating: tubing finished with a high emissivity rated, corrosion resistant, black coating.]

- [SMT and SST models: Heat exchanger tubing of 4-inch diameter, 16 ga. wall thickness, 304L stainless-steel.]

- [MTSA/MTUA and GQ models: Heat exchanger tubing of 4-inch diameter, 16 ga. (.065") wall thickness, heat treated aluminized-steel, and meet MIL 500 hour salt spray test.]

H.	Tubing Connections:

1.	[MT and ST models: Clamps of two layers of 18 ga. (.052") thick aluminized-steel, 8" length, compression coupling design having uniform draw and pressure, with four (4) 5/8"-11x2" zinc plated carriage bolts and nuts to hold 65 foot-pounds torque.]

2.	[SMT and SST models: Clamps of two layers of stainless-steel, 8" length, compression coupling design having uniform draw and pressure, with four (4) 5/8"-11x2" stainless-steel carriage bolts and nuts to hold 65 foot-pounds torque.]

3.	[MTSA/MTUA and GQ models: Flared/swaged joints with 3-inch tube overlap. Flared end of tubes have two (2) clearance holes for two (2) multi-metal self-drilling screws.]

4.	[MTSA/MTUA and GQ models: The coupler joining burner and combustion chamber tube 16 ga. (.065") wall thickness aluminized-steel, 8" length, meet MIL 500 hour salt spray test, and have two (2) sets of two (2) clearance holes for two (2) multi-metal self-drilling screws.]

I.	Reflector:

1.	Reflector geometrically shaped for not less than 91.7% reflectional efficiency.

2.	Material:

a.	[MT, MTSA/MTUA, ST and GQ models: Reflector .025" thick, #3003H25 aluminum mill finish.]

b.	[SMT and SST models: Reflector 20 ga., 304 stainless-steel.]

3.	Mounting and Rotation:

a.	Reflector mountable to heater without use of tools.

b.	Reflector mounting permit heater expansion, minimizing noise and/or rattles.

c.	[MT, MTSA/MTUA, ST and GQ models: Reflector held by .229" diameter nickel plated steel wire hangers.]

d.	[MT and ST models: Reflector sections independently rotatable from all other sections, or overlapped between, or combination of both over system length.]

e.	[SMT and SST models: Mounting incorporate ability to rotate reflector up to 45 degrees, in either direction with tubing center as the axis of rotation.]

J.	Venting:

1.	[Unvented: Heaters indirectly vented by natural or mechanical means with supply and exhaust of at least 4 CFM per 1000 Btu/hour input of installed heaters.]

2.	[Vented: Heaters directly vented outdoors with insulated flue pipe.]

a.	[Gravity-vented.]

b.	[Sidewall-vented.]

3.	[Connector at exit end of emitter/heat exchanger tubing for vent-pipe connection.]

4.	[Dual venting on one thermostat: two (2) heaters controlled by one thermostat.]

5.	[Dual venting with two thermostats: concentric vent for two (2) heaters controlled by two (2) thermostats with vent cap for individual vent coupler.]

6.	[Vent Terminal:]

a.	[Vertical.]

b.	[Horizontal.]

K.	Capacities and Characteristics:

1.	Gas Input:

- [Specify MBTUH (1000 Btu/hr).]

- Single-stage models: 40, 45, 50, 55, 60, 65, 70, 75, 80, 85, 90, 95, 100, 105, 110, 115, 120, 125, 130, 135, 140, 145, 150, 155, 160, 165, 170, 175, 180, 185, 190, 195, 200 MBTUH.

- Gas Supply Piping Connection: 1/2 inch FPT.

- Gas Connector: 36” long stainless steel flexible gas supply connector.

4.	Altitude:

a.	[Sea level to 2000 feet.]

b.	[Above 2000 feet.]

5.	Total Combustion and Emitter/Heat Exchanger Tubing length:

- [Specify from 10 to 70 feet in 5-foot increments.]

- [Single-stage 40 MBTUH models: 10 feet.],

- [Single-stage 40 MBTUH models: 15 feet.],

- [2-stage 85/65 MBTUH models and single-stage 40 thru 85 MBTUH models: 20 feet.],

- [2-stage 85/65 MBTUH models and single-stage 65 thru 85 MBTUH models: 25 feet.],

- [2-stage 100/65 MBTUH and natural gas 125/95 MBTUH models and single-stage 65 thru 100 MBTUH and natural gas 105 thru 130 MBTUH models: 30 feet.],

- [2-stage 100/65 MBTUH and natural gas 125/95 MBTUH models and single-stage 65 thru 100 MBTUH and natural gas 105 thru 130 MBTUH models: 35 feet.],

- [2-stage 100/65, 125/95 and 150/100 MBTUH models and single-stage 65 thru 150 MBTUH models: 40 feet.],

- [2-stage 125/95 and 150/100 MBTUH models and single-stage 100 thru 150 MBTUH models: 45 feet.],

- [2-stage 125/95, 150/100, 175/125 and 200/145 MBTUH models and single-stage 100 thru 200 MBTUH models: 50 feet.],

- [2-stage 150/100, 175/125 and 200/145 MBTUH models and single-stage 150 thru 200 MBTUH models: 55 feet.],

- [2-stage 150/100, 175/125 and 200/145 MBTUH models and single-stage 150 thru 200 MBTUH models: 60 feet.],

- [2-stage 175/125 and 200/145 MBTUH models and single-stage 150 thru 200 MBTUH models: 65 feet.],

- [2-stage 175/125 and 200/145 MBTUH models and single-stage 150 thru 200 MBTUH models: 70 feet.]

6.	Configuration of Emitter/Heat Exchanger Tubing:

a.	[Straight Tube System.]

b.	[U-Tube System.]

c.	[L-Shaped System.]

L.	Accessories:

1.	Manual gas ball valve.

2.	Mounting chain with S-hooks.

3.	Indoor venting kit.

4.	4-inch roof venting cap for single heater.

5.	4-inch wall venting kit for single heater.

6.	[MT, MTSA/MTUA, ST and GQ natural gas models: Inlet air collar to connect combustion air ducting to burner.]

7.	[MT, MTSA/MTUA, ST and GQ models: Blower motor enclosure, factory installed, for harsh environments.]

8.	4-inch roof combustion air supply kit for single heater.

9.	4-inch wall combustion air supply kit for single heater.

10.	90-degree 4-inch heater emitter/heat exchanger elbow for making "L" shaped heater systems.

11.	4x4x5-inch Y-coupler for dual venting to join two (2) heaters to one common 5-inch vent using one (1) thermostat.

12.	5-inch roof vent cap for dual venting two (2) heaters.

13.	5-inch wall vent kit for dual venting two (2) heaters.

14.	4x4x6-inch individual vent coupler (Y) to join two (2) heaters to one common or individual 6-inch vent using one (1) or (2) thermostats.

15.	6-inch roof vent cap for dual venting two (2) heaters.

16.	6-inch wall vent kit for dual venting two (2) heaters.

17.	Vent cap for individual vent coupler to independently vent two (2) heaters thru one (1) 6-inch roof vent when using two (2) thermostats.

18.	6-inch roof supply kit to supply combustion air for two (2) heaters.

19.	6-inch wall supply kit to supply combustion air for two (2) heaters.

20.	U-bend reflector assembly.

21.	Corner reflector assembly for 90-degree heater elbow.

22.	Reflector side extension assembly.

23.	End cap for reflector.

24.	Outdoor kit.

25.	Decorative grille kit.