Copyright 2013 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to Solaronics, Inc. ("Licensee") ARCOM007.

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Solaronics, Inc., 3720 Lapeer Rd., Auburn Hills, MI 48326; Phone: (800) 223-5335; Fax: (248) 651-0357; Website: http://solaronicsusa.com; Email: sales@solaronicsusa.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 235523.13 - LOW-INTENSITY, GAS-FIRED, RADIANT HEATERS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

If applying for LEED certification, LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1, in which Section 6.5.8 - "Radiant Heating Systems" requires that radiant heat be used to heat unenclosed spaces except loading docks equipped with air curtains.

GENERAL

SUMMARY

See "Design Considerations" Article in the Evaluations for an explanation of the different heater configurations.

Section includes low-intensity, gas-fired, [forced-draft] [draft-induced] [multiple-burner] radiant heaters.

ACTION SUBMITTALS

Product Data: For each type of product.

Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

Shop Drawings:

Retain first subparagraph below if equipment is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data is required as another way to verify equipment's compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

Signed, sealed, and prepared by or under the supervision of a qualified professional engineer.

Include plans, elevations, sections, and [mounting] [attachment] details.

Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Detail fabrication and assembly of low-intensity, gas-fired, radiant heaters, as well as procedures and diagrams.

Retain option in subparagraph below if thermostat is specified in this Section; delete if thermostats for these units are specified in Section 230923.27 "Temperature Instruments."

Include diagrams for power[, signal, and control] wiring.

INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

Coordination Drawings: Plans, elevations, and other details, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

Structural members to which equipment will be attached.

Gas piping to heater installations

Retain first subparagraph below if thermostats are not specified in Section 230923.27 "Temperature Instruments."

Thermostats and wiring to heaters.

Heater locations and clearance requirements.

Other suspended ceiling components including the following:

Lighting fixtures.

Air outlets and inlets.

Sprinklers.

Mobile crane.

<Insert item>.

Field quality-control reports.

Sample Warranty: For manufacturer's special warranties.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For gas-fired, radiant heaters to include in emergency, operation, and maintenance manuals.

MAINTENANCE MATERIAL SUBMITTALS

Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Igniter: [One] <Insert number> direct spark burner igniter(s) for each style of low-intensity, gas-fired, radiant heater furnished.

WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

Manufacturer's Special Warranty: Manufacturer agrees to repair or replace components of radiant heaters that fail in materials or workmanship within specified warranty period.

See the Forced-Draft Radiant Heater Product Comparison Matrix in the Evaluations for a comparison of warranties offered among manufacturers listed. Verify available warranties and warranty periods.

Warranty Period: All warranty periods listed below are from date of Substantial Completion.

Burner Core: 10 years.

Combustion and Emitter Tubes: [Five] [10] years.

Heater Controls: [One] [Three] year(s).

PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

PERFORMANCE REQUIREMENTS

CSA certified, with CSA Seal and certification number clearly visible on units indicating compliance with ANSI Z83.20/CSA 2.34.

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

FORCED-DRAFT HEATERS

Copy this article and re-edit for each product.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Solaronics' "Suntube IV-GQ Series" is a single-stage tube heater with slip-fit tube connection package. See www.solaronicsusa.com/suntube-iv-gq-single-stage/.

"Suntube IV-STG-VM Series" is a single-stage tube heater with heavy-duty tube clamp connection package. See www.solaronicsusa.com/suntube-iv-stg-vm-single-stage/.

"Suntube IV-STG-VM-OS Series" is a single-stage tube heater with heavy-duty tube clamp connection package.

"Suntube IV-SST Series" is a single-stage tube heater for harsh environment applications. See www.solaronicsusa.com/suntube-iv-sst-single-stage/.

"True Dual MTSA Series" is a two-stage tube heater with slip-fit tube connection package. See www,solaronicsusa.com/true-dual-mtsa-2-stage/.

"True Dual MTS Series" is a two-stage tube heater with heavy-duty tube clamp connection package. See www.solaronicsusa.com/true-dual-mts-2-stage/.

"True Dual MTS-OS Series" is a two-stage tube heater with heavy-duty tube clamp connection package.

"True Dual SMTS Series" is a two-stage tube heater for harsh environment applications. See www.solaronicsusa.com/true-dual-smts-2-stage/.

Basis-of-Design Product: Subject to compliance with requirements, provide Solaronics, Inc.; [Suntube IV-GQ] [Suntube IV-STG-VM] [Suntube IV-STG-VM-OS] [Suntube IV-SST] [True Dual MTSA] [True Dual MTS] [True Dual MTS-OS] [True Dual SMTS] Series or comparable product by one of the following:

Detroit Radiant Products Company.

Roberts-Gordon, Inc.

Space-Ray; a division of Gas-Fired Products Inc.

<Insert manufacturer's name>.

Description: Factory-assembled, [indoor] [outdoor], overhead-mounted, electrically controlled, low-intensity, infrared radiant heating units using gas combustion. Heater to have all necessary factory-installed wiring and piping required prior to field installation and startup.

Standards:

ANSI Z83.20 - Gas-Fired High Intensity Infrared Heaters.

NFPA 54 - National Fuel Gas Code.

NFPA 70 - National Electrical Code.

UL 486A - Wire Connectors and Soldering Lugs for Use with Copper Conductors.

UL 486B - Wire Connectors for Use with Aluminum Conductors.

Fuel Type: Design burner for [natural] [propane] gas having characteristics same as those of gas available at Project site.

Burner Assembly:

Retain one of two "Combustion-Air Inlet" subparagraphs below. Heaters built to work indoors can be ducted to receive outdoor air if needed.

Combustion-Air Inlet: Ducted horizontal to outdoors through sidewall with vent caps.

Combustion-Air Inlet: Ducted vertical to outdoors through roof with vent caps.

Burner Control Housing: [Stainless steel] [Corrosion-resistant, aluminized steel].

Retain first subparagraph below if burner control housing is totally enclosed.

Totally enclosed with [stainless steel] [steel] access cover.

Sight glass for visual inspection of burner.

Burner Ignition:

Direct spark ignition with electronic flame safety.

Direct spark ignition durable to resist breakage.

Burner Blower:

Motor: Balanced-rotor, thermally protected, fan-cooled, and permanently lubricated sealed ball bearings.

Blower Impeller: Statically and dynamically balanced.

Capable of drawing in outside combustion air without using additional supply fans.

Burner Safety Controls:

Gas Control Valve:

Retain one of first two subparagraphs below.

Two-stage, regulated redundant-solenoid 24-VAC electric gas valve containing pressure regulator and manual shutoff in one body, and no pilot.

Single-stage, regulated redundant-solenoid 115-VAC electric gas valve containing pressure regulator, and no pilot.

Blocked Vent Safety: Differential pressure switch in burner safety circuit to stop burner operation with high discharge pressure or insufficient combustion air.

Indicator Lights: Burner-on indicator light.

Safety Shutoff: Automatic shut-off of gas flow to burner when gas supply or power supply interrupted.

Combustion Chamber: 4-inch- (100-mm-) diameter, [14-gauge] [or] [16-gauge] [or] [Aluminized 409 stainless steel] [or] [Aluma Therm - aluminized titanium-coated] [or] [BHT] heat treaded or finished with a high-emissivity rated, high-temperature, corrosion-resistant, black coating.

In "Heat Exchangers" Paragraph below, retain 16-gauge heat-treated aluminized steel if "Suntube IV-GQ Series" is selected; retain 12-gauge black steel if "Suntube IV-STG0VM Series" is selected; retain 16-gauge 304L stainless steel if "Suntube IV-SST Series" is selected.

Heat Exchangers: [12-gauge black steel] [or] [16-gauge heat-treated aluminized steel] [or] [16-gauge 304L stainless steel].

See "Emitter Tubing Material" Article in the Evaluations for an explanation of pros and cons of various emitter tube materials in use. Also see manufacturer's documentation to determine which materials best suit specific application requirements.

Emitter Tube: 4-inch- (100-mm-) diameter, [12] [16]-gauge, [aluminized] [hot-rolled] [stainless] [titanium-coated aluminized] steel tubing with heat treated or high-emissivity, high-temperature, corrosion-resistant external finish.[ Emitter tubing to be equipped with baffles to maximize heating efficiency.]

Tubing Connections: [Interlocking flare joints with multi metal self-drilling screws] [Compression couplings made from aluminized or stainless steel].

[90] [180]-degree-bend emitter steel tubing with heat-treated or high-emissivity, high-temperature, corrosion-resistant external finish.

Retain "Exhaust Vent Termination" Subparagraph below if emitter tubes are to be vented outdoors. Venting emitter tubes is not necessary as long as a minimum of 4 cfm/1000 Btu/h (1.8 L/s/293 W) is maintained in the space where the radiant heater is utilized.

Exhaust Vent Termination: [Vertical through roof] [Horizontal though side wall] with vent caps.

Reflector: 0.025-inch- (0.635-mm-) thick, no. 3003H25 aluminum mill finish or 0.024-inch (610- mm) Type 304 stainless steel with a geometrically designed configuration having not less than 91.7 percent reflectional efficiency, to be held by a 0.229-inch- (5.8-mm-) diameter nickel-plated steel wire hanger, 16-gauge Type 304 stainless steel brackets used for stainless steel reflectors. Reflectors or entire heater to accommodate rotational adjustment from horizontal to a minimum 30-degree tilt from vertical.

Accessories:

Verify that required accessories retained in subparagraphs below are available from manufacturers retained in "Manufacturers" or "Basis-of-Design Product" Paragraph above. See the Forced-Draft Radiant Heater Product Comparison Matrix in the Evaluations for more information.

Reflector Extension Shields: Same material as reflectors, arranged for fixed connection to lower reflector lip and rigid support to provide 100 percent cutoff of direct radiation from tubing at angles greater than 30 degrees from vertical.

Manual gas ball valve.

Hanger chain with "S" hooks.

Rigid mounting kits.

Outdoor use conversion kit.

4-inch (100-mm) roof combustion air supply kit for single heater.

4-inch (100-mm) wall venting kit for single heater.

Inlet air collar to connect combustion air ducting to burner.

Blower motor enclosure factory installed.

4-inch (100-mm) roof vent kit for single heater.

4-inch (100-mm) wall combustion air supply kit for single heater.

90-degree 4-inch (100-mm) heater emitter/heat exchanger elbow for making "L" shaped heater systems.

4- by 4- by 5-inch (102- by 102- by 125-mm) Y-coupler for dual venting to join two heaters to one common 5-inch (125-mm) vent using one thermostat.

5-inch (125-mm) roof vent cap for dual venting two heaters.

5-inch (125-mm) wall vent kit for dual venting two heaters.

4- by 4- by 6-inch (102- by 102- by 150-mm) individual vent coupler (Y) to join two heaters to one common or individual 6-inch (150-mm) vent using one or two thermostats.

6-inch (150-mm) roof vent cap for dual venting two heaters.

6-inch (150-mm) wall vent kit for dual venting two heaters.

6-inch (150-mm) roof supply kit to supply combustion air for two heaters.

6-inch (150-mm) wall supply kit to supply combustion air for two heaters.

U-bend reflector assembly.

Corner reflector assembly for 90-degree heater elbow.

Reflector side extension assembly.

End cap for reflector.

Decorative grille kit.

Protective guard kit.

Recessed ceiling kit.

If Project has more than one type or configuration of forced-draft, low-intensity, gas-fired, radiant heater, delete "Capacities and Characteristics" Paragraph below and schedule radiant heaters on Drawings.

Capacities and Characteristics:

Gas Input, Single-Stage Models: [40 Mbtu/h (11723 kW)], [45 Mbtu/h (13188 kW)], [50 Mbtu/h (14654 kW)], [55 Mbtu/h (16119 kW)], [60 Mbtu/h (17584 kW)], [65 Mbtu/h (19050 kW)], [70 Mbtu/h (20515 kW)] [75 Mbtu/h (21980 kW)], [80 Mbtu/h (23445 kW)], [85 Mbtu/h (24911 kW)], [90 Mbtu/h (26376 kW)], [95 Mbtu/h (27842 kW)], [100 Mbtu/h (29307 kW)], [105 Mbtu/h (30772 kW)], [110 Mbtu/h (32238 kW)], [115 Mbtu/h (33703 kW)], [120 Mbtu/h (35169 kW)], [125 Mbtu/h (36634 kW)], [130 Mbtu/h (38099 kW)], [135 Mbtu/h (39565 kW)], [140 Mbtu/h (41030 kW)], [145 Mbtu/h (42495 kW)], [150 Mbtu/h (43960 kW)], [155 Mbtu/h (45426 kW)], [160 Mbtu/h (46891 kW)], [165 Mbtu/h (48357 kW)], [170 Mbtu/h (49822 kW)], [175 Mbtu/h (51287 kW)], [180 Mbtu/h (52753 kW)], [185 Mbtu/h (54218 kW)], [190 Mbtu/h (55684 kW)], [195 Mbtu/h (57149 kW)], [200 Mbtu/h (58614 kW)].

Fuel-Supply Connection: 1/2 inch (15 mm).

Retain "Combustion-Air Fan Motor Size" Subparagraph below if combustion-air supply fan is not an integral part of the burner assembly and is mounted as an exterior component.

Combustion-Air Fan Motor Size: <Insert value> hp.

Volts: 120 V.

Phase: Single.

Hertz: 60.

Full-Load Amperes:3.0 A

DRAFT-INDUCED HEATERS

Copy this article and re-edit for each product.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Combustion Research Corporation.

Detroit Radiant Products Company.

Roberts-Gordon, Inc.

Schwank Inc.

Space-Ray; a division of Gas-Fired Products Inc.

Superior Radiant Products Ltd.

<Insert manufacturer's name>.

Description: Factory-assembled, [indoor] [outdoor], overhead-mounted, electrically controlled, low-intensity, infrared radiant heating units using gas combustion. Heater to have all necessary factory-installed wiring and piping required prior to field installation and startup.

Fuel Type: Design burner for [natural] [propane] gas having characteristics same as those of gas available at Project site.

Burner Assembly:

Retain one of three "Combustion-Air Inlet" subparagraphs below. Heaters built to work indoors can be ducted to receive outdoor air if needed.

Combustion-Air Inlet: Non-ducted, unvented.

Combustion-Air Inlet: Ducted horizontal to outdoors through sidewall with vent caps.

Combustion-Air Inlet: Ducted vertical to outdoors through roof with vent caps.

In "Burner Control Housing" Paragraph below, retaining "Stainless steel" option may limit the number of qualified manufacturers.

Burner Control Housing: [Stainless steel] [Corrosion-resistant, aluminized steel] [Steel].

Retain first subparagraph below if burner control housing is totally enclosed.

Totally enclosed with [stainless steel] [steel] access cover.

Sight glass for visual inspection of burner.

Retain "Finish" Subparagraph below if retaining "Steel" option in "Burner Control Housing" Subparagraph above.

Finish: [Enameled finish] [or] [powder-coated finish].

Retain "Burner," "Ignition System," and Combustion Blower Fan" subparagraphs below if these are critical Project requirements. Including these requirements may limit competition.

Burner: [Stainless steel] [One-piece cast iron].

Ignition System: [Silicon carbide hot-surface igniter] [Direct spark] [24/25-V ac] [115/120-V ac] with flame rod sensing capabilities[ and self-diagnostic control module].

Retain "Combustion Blower Fan" Subparagraph below if combustion air is supplied by a blower. The blower may be integral to the burner assembly or an external component.

Combustion Blower Fan: Dynamically balanced, direct-driven, forward-curved fan with [cast-aluminum-alloy] [stainless steel] <Insert material> impeller and [aluminized-]steel housing, with a minimum temperature rating of 450 deg F (232 deg C).

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

Motors: General requirements for motors are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Motor: Resilient-mounted, capacitor-start-capacitor-run type with sealed ball bearings; totally enclosed, non-ventilated type with internal thermal protection.

Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Combustion Chamber: 4-inch- (100-mm-) diameter, [12] [16]-gauge, [aluminized] [titanium-coated aluminized] [stainless] [hot-rolled]-steel tubing with high-emissivity, high-temperature, corrosion-resistant external finish. Chambers to be equipped with sight glass for burner and pilot flame observation.

See "Emitter Tubing Material" Article in the Evaluations for an explanation of pros and cons of various emitter tube materials in use. Also see manufacturer's documentation to determine which materials best suit specific application requirements.

Emitter Tube: [4-inch- (100-mm-)] [3-inch- (76-mm-)] diameter, [12] [16]-gauge, [aluminized] [hot-rolled] [stainless] [titanium-coated aluminized]-steel tubing with high-emissivity, high-temperature, corrosion-resistant external finish.[ Emitter tubing to be equipped with baffles to maximize heating efficiency.]

Tubing Connections: [Stainless steel threaded couplings] [Interlocking flare joints with stainless steel draw bolts] [Compression couplings made from aluminized or stainless steel].

[90] [180]-degree-bend emitter steel tubing with high-emissivity, high-temperature, corrosion-resistant external finish.

Vacuum Exhaust Fan: Dynamically balanced, direct-driven, [cast-aluminum-alloy] [stainless steel] impeller in aluminized-steel housing, isolated from emitter tubing exhaust system by high-temperature flexible vibration isolation connector. Fan and connector to have a minimum temperature rating of 450 deg F (232 deg C).

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

Motors: General requirements for motors are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Motor: Resilient-mounted, capacitor-start-capacitor-run type with sealed ball bearings; totally enclosed, non-ventilated type with internal thermal protection.

Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Retain one or more optional accessories in three subparagraphs below.

Balancing Dampers: Plate type, mounted in cast, double-flange fitting with vacuum test plug.

Filter: Cartridge type for mounting on burner housing.

Retain "Exhaust Vent Termination" Subparagraph below if emitter tubes are to be vented outdoors. Venting emitter tubes is not necessary as long as a minimum of 4 cfm/1000 Btu/h (1.8 L/s/293 W) is maintained in the space where the radiant heater is utilized

Exhaust Vent Termination: [Vertical through roof] [Horizontal through side-wall] with vent caps.

Reflector: [Polished aluminum] [Polished stainless steel] [High-grade steel with a heat- and corrosion-resistant, hot-bonded, aluminum-silicon alloy coating], with end caps. Shape to control radiation from tubing for uniform intensity at floor level with 100 percent cutoff above centerline of tubing. Reflectors or entire heater to accommodate rotational adjustment from horizontal to a minimum 30-degree tilt from vertical.

Accessories:

Verify that required accessories retained in subparagraphs below are available from manufacturers retained in "Manufacturers" or "Basis-of-Design Product" Paragraph above.

Reflector Extension Shields: Same material as reflectors, arranged for fixed connection to lower reflector lip and rigid support to provide 100 percent cutoff of direct radiation from tubing at angles greater than 30 degrees from vertical.

Protective grilles mounted to reflectors to protect emitter tubing.

Stainless steel flexible connector with manual valve for gas supply.

Hanger chain with "S" hooks.

3/16-inch- (5-mm-) diameter, [galvanized][aluminized]-steel wire tubing hangers and reflector supports.

Rigid mounting kits.

Outdoor use conversion kit.

Clearance warning plaque.

If Project has more than one type or configuration of draft-induced, low-intensity, gas-fired, radiant heater, delete "Capacities and Characteristics" Paragraph below and schedule radiant heaters on Drawings.

Capacities and Characteristics:

Gas Input: <Insert Btu/h (kW)>.

Gas Output: <Insert Btu/h (kW)>.

Fuel-Supply Connection: <Insert inches (mm)>.

Retain "Combustion-Air Fan Motor Size" Subparagraph below if combustion-air supply fan is not an integral part of the burner assembly and is mounted as an exterior component. Not all draft-induced heaters have combustion-air fans. Some rely solely on the induced draft of the vacuum exhaust fan.

Combustion-Air Fan Motor Size: <Insert value> hp.

Volts: [120] [208] [230] <Insert value> V.

Phase: [Single] [Three].

Hertz: 60.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Vacuum Exhaust Fan Motor Size: <Insert value> hp.

Volts: [120] [208] [230] <Insert value> V.

Phase: [Single] [Three].

Hertz: 60.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

MULTIPLE-BURNER HEATERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Combustion Research Corporation.

Detroit Radiant Products Company.

Roberts-Gordon, Inc.

<Insert manufacturer's name>.

Description: Factory-assembled, [indoor] [outdoor], overhead-mounted, electrically controlled, low-intensity, infrared radiant heating units using gas combustion. Heater to have all necessary factory-installed wiring and piping required prior to field installation and startup.

Fuel Type: Design burner for [natural] [propane] gas having characteristics same as those of gas available at Project site.

Copy "Burner Assembly" Paragraph below and re-edit for each type of burner used.

Burner Assembly: <Insert drawing designation>.

Retain one of three "Combustion-Air Inlet" subparagraphs below. Heaters built to work indoors can be ducted to receive outdoor air if needed.

Combustion-Air Inlet: Non-ducted, unvented.

Combustion-Air Inlet: Ducted horizontal to outdoors through sidewall with vent caps.

Combustion-Air Inlet: Ducted vertical to outdoors through roof with vent caps.

In "Burner Control Housing" Paragraph below, retaining "Stainless steel" option may limit the number of qualified manufacturers.

Burner Control Housing: [Stainless steel] [Corrosion-resistant, aluminized steel] [Steel].

Retain first subparagraph below if burner control housing is totally enclosed.

Totally enclosed with [stainless steel] [steel] access cover.

Sight glass for visual inspection of burner.

Retain "Finish" Subparagraph below if retaining "Steel" option in "Burner Control Housing" Subparagraph above.

Finish: [Enameled finish] [or] [powder-coated finish].

Retain "Burner," "Ignition System," and "Combustion Blower Fan" subparagraphs below if these are critical Project requirements. Including these requirements may limit competition.

Burner: [Stainless steel] [One-piece cast iron].

Ignition System: [Silicon carbide hot-surface igniter] [Direct spark] [24/25-V ac] [115/120-V ac] with flame rod sensing capabilities[ and self-diagnostic control module].

Retain "Combustion Blower Fan" Subparagraph below if combustion air is supplied by a blower. The blower may be integral to the burner assembly or an external component.

Combustion Blower Fan: Dynamically balanced, direct-driven, forward-curved fan with [cast-aluminum-alloy] [stainless steel] <Insert material> impeller and [aluminized-]steel housing, with a minimum temperature rating of 450 deg F (232 deg C).

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

Motors: General requirements for motors are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Motor: Resilient-mounted, capacitor-start-capacitor-run type with sealed ball bearings; totally enclosed, non-ventilated type with internal thermal protection.

Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Combustion Chamber: 4-inch- (100-mm-) diameter, [12] [16]-gauge, [aluminized] [titanium-coated aluminized] [stainless] [hot-rolled]-steel tubing with high-emissivity, high-temperature, corrosion-resistant external finish. Chambers to be equipped with sight glass for burner and pilot flame observation.

See "Emitter Tubing Material" Article in the Evaluations for an explanation of pros and cons of various emitter tube materials in use. Also see manufacturer's documentation to determine which materials best suit specific application requirements.

Emitter Tube: [4-inch- (100-mm-)] [3-inch- (76-mm-)] diameter, [12] [16]-gauge, [aluminized] [hot-rolled] [stainless] [porcelain-lined] [titanium-coated aluminized]-steel tubing with high-emissivity, high-temperature, corrosion-resistant external finish.[ Emitter tubing to be equipped with baffles to maximize heating efficiency.]

Tubing Connections: [Stainless steel threaded couplings] [Interlocking flare joints with stainless steel draw bolts] [Compression couplings made from aluminized or stainless steel].

[90-degree bends] [180-degree bends] [Tee fittings] [Cross fittings] made from [stainless steel] with corrosion-resistant, high-temperature black coating.

Condensing Tubing: 4-inch- (100-mm-) diameter, stainless steel tubing with high-emissivity, high-temperature, corrosion-resistant external finish.

Vacuum Exhaust Fan: Dynamically balanced, direct-driven, [cast-aluminum-alloy] [stainless steel] impeller in aluminized-steel housing, isolated from emitter tubing exhaust system by high-temperature flexible vibration isolation connector. Fan and connector to have a minimum temperature rating of 450 deg F (232 deg C).

See [Section 230548 "Vibration and Seismic Controls for HVAC"] [Section 230548.13 "Vibration Controls for HVAC"] for mounting vacuum exhaust fan.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

Motors: General requirements for motors are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Motor: Resilient-mounted, capacitor-start-capacitor-run type with sealed ball bearings; totally enclosed, non-ventilated type with internal thermal protection.

Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Retain one or both optional accessories in two subparagraphs below.

Balancing Dampers: Plate type, mounted in cast, double-flange fitting with vacuum test plug.

Filter: Cartridge type for mounting on burner housing.

Exhaust Vent Termination: [Vertical through roof] [Horizontal though side wall] with vent caps.

Retaining third option in "Reflector" Subparagraph below will limit the suppliers to Schwank.

Reflector: [Polished aluminum] [Polished stainless steel] [High-grade steel with a heat- and corrosion-resistant, hot-bonded, aluminum-silicon alloy coating], with end caps. Shape to control radiation from tubing for uniform intensity at floor level with 100 percent cutoff above centerline of tubing. Reflectors to accommodate rotational adjustment from horizontal to a minimum 30-degree tilt from vertical.

Accessories:

Verify that required accessories retained in subparagraphs below are available from manufacturers retained in "Manufacturers" or "Basis-of-Design Product" Paragraph above.

Reflector Extension Shields: Same material as reflectors, arranged for fixed connection to lower reflector lip and rigid support to provide 100 percent cutoff of direct radiation from tubing at angles greater than 30 degrees from vertical.

Protective grilles mounted to reflectors to protect emitter tubing.

Stainless steel flexible connector with manual valve for gas supply.

Hanger chain with "S" hooks.

3/16-inch- (5-mm-) diameter, [galvanized][aluminized]-steel wire tubing hangers and reflector supports.

Rigid mounting kits.

Outdoor use conversion kit.

Clearance warning plaque.

If Project has more than one type of burner assembly, delete "Capacities and Characteristics" Paragraph below and schedule burner assemblies on Drawings.

Capacities and Characteristics:

Gas Input: <Insert Btu/h (kW)>.

Gas Output: <Insert Btu/h (kW)>.

Fuel-Supply Connection: <Insert inches (mm)>.

Retain "Combustion-Air Fan Motor Size" Subparagraph below if combustion-air supply fan is not an integral part of the burner assembly and is mounted as an exterior component.

Copy and re-edit "Combustion-Air Fan Motor Size" Subparagraph below for every type of combustion-air fan motor used.

Combustion-Air Fan Motor Size: <Insert value> hp.

Volts: [120] [208] [230] <Insert value> V.

Phase: [Single] [Three].

Hertz: 60.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Vacuum Exhaust Fan Motor Size: <Insert value> hp.

Volts: [120] [208] [230] <Insert value> V.

Phase: [Single] [Three].

Hertz: 60.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

CONTROLS AND SAFETIES

Gas Control Valve: [Single] [Two]-stage, regulated redundant 24-V ac gas valve that contains pilot solenoid valve, electric gas valve, pilot filter, pressure regulator, pilot shutoff, and manual shutoff all in one body.

Failure Safeguards: 100 percent shutoff of gas flow in the event of flame or power failure.

Prepurge of [15] [30] [45] seconds of air control system prior to burner ignition.

Safety lockout of burner after [three consecutive ignition failures] [flame is not reestablished within trial ignition period].

Blocked Vent Safety: Differential pressure switch in burner safety circuit to stop burner operation with high discharge or suction pressure.

Control Panel Interlock: Stops burner if panel is open.

Indicator Lights: ["Airflow-on"] [and] ["burner-on"] indicator lights.

Retain one of three "Thermostat" paragraphs below. Note that thermostats may not be supplied with some units.

Thermostat: Devices and wiring are specified in Section 230923.27 "Temperature Instruments."

Thermostat: Single-stage, wall-mounted type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

Control Transformer: Integrally mounted.

Thermostat: Two-stage, wall-mounted type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

Control Transformer: Integrally mounted.

EXECUTION

EXAMINATION

Examine structures, substrates, areas and conditions, with Installer present, for compliance with requirements for installation tolerances, required clearances, and other conditions affecting performance of the Work.

Examine roughing-in for fuel-gas piping to verify actual locations of piping connections before equipment installation.

Prepare written report, endorsed by Installer, listing conditions detrimental to performance of the Work.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Equipment Installation: Install gas-fired, radiant heaters and associated gas features and systems in accordance with [NFPA 54] [CSA B149.1].

Suspended Units: [Suspend from substrate using chain hanger kits and building attachments] [Mount to substrate using manufacturer's rigid mounting kits or custom fabricated brackets].

Retain first subparagraph below if Project site is in a seismic area.

Restrain the unit to resist seismic acceleration. Comply with requirements for seismic-restraint devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

Comply with requirements for hangers and supports specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

Maintain manufacturers' recommended clearances for combustibles.

CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

Gas Piping: Comply with [Section 231123 "Facility Natural-Gas Piping."] [Section 231126 "Facility Liquefied-Petroleum Gas Piping."] Connect gas piping to gas train inlet; provide union with enough clearance for burner removal and service.

Gas Connections: Connect gas piping to radiant heaters in accordance with [NFPA 54] [CSA B149.1].

Where installing piping adjacent to gas-fired, radiant heaters, allow space for service and maintenance.

Vent Connections: Comply with Section 233113 "Metal Ducts" and with Section 235100 "Breechings, Chimneys, and Stacks."

Electrical Connections: Comply with applicable requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

Install electrical devices furnished with heaters but not specified to be factory mounted.

FIELD QUALITY CONTROL

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

Verify bearing lubrication.

Verify proper motor rotation.

Test Reports: Prepare a written report to record the following:

Test procedures used.

Test results that comply with requirements.

Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

Gas-fired, radiant heaters will be considered defective if they do not pass tests and inspections.

Prepare test and inspection reports.

Retain "Adjusting" and "Demonstration" articles below for multiple-burner systems.

ADJUSTING

Adjust initial-temperature set points.

Adjust burner and other unit components for optimum heating performance and efficiency.

DEMONSTRATION

[Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain gas-fired, radiant heaters.

END OF SECTION 235523.13